## Series Scale Up
Community Properties |  |  | *input by user
Demand | 50000 | gal/day
Contaminated Water Source Properties
Q | 0.13142 | m3/min
Cin | 82.2 | µg/L
Cout | 5 | µg/L
Desired Percent Removal | 93.9173 | %
Final Design Results (SI Units) |  |  | Final Design Results (BG Units)
n | 3 | columns | n | 3 | columns
Loading Rate | 1.1655 | m/hr | Loading Rate | 3.8237 | ft/hr
Area | 6.766 | m2 | Area | 72.8282 | ft2
Diameter | 2.9351 | m | Diameter | 9.6295 | ft
Bed Height | 4 | m | Bed Height | 13.1234 | ft
Bed Volume | 27.0639 | m3 | Bed Volume | 955.7511 | ft3
Bead Height | 2 | m | Bead Height | 6.5617 | ft
Total Vessel Volume | 40.5958 | m3 | Total Vessel Volume | 1433.6266 | ft3
Cob Utilization Rate | 215.7801 | kg/day | Cob Utilization Rate | 475.7952 | lb/day
Change Out Period | 30 | days | Service Time | 30 | days
Mass of Corn Required | 6473.404 | kg | Mass of Corn Required | 7.1369 | tons

## Final Dimension Adjustments
Preliminary Design Results
n | 2 | columns
Loading Rate | 0.063942 | m/hr
Area | 2.0553 | m2
Diameter | 1.6177 | m
Height | 0.02286 | m
Volume | 0.046985 | m3
Corn Cob Utilization | 215.7801 | kg/day
Dimension Adjustments for Change Out
Change out period | 30 | days
S.F. for Backwash | 1.2
Volume | 27.0639 | m3
Height | 4 | m
Diameter | 2.9351 | m
Area | 6.766 | m2
Loading Rate | 1.1655 | m/hr
Bead Height | 2 | m
Total Column Height | 6 | m
Total Column Volume | 40.5958 | m3

## Bed Depth Service Time
Lab Column Properties |  |  |  |  | Service Time, minutes, for % contaminant remaining
Flow Rate | 0.54 | mL/min | Column # | Cumulative Bed Depth (m) | 6% | 10% | 50% | 60% | 70% | 75%
Corn Bed Depth | 0.9 | in. | 1 | 0.02286 | 12.5 | 15 | 49 | 61 | 71 | 76
Diameter | 1 | in. | 2 | 0.04572 | 98 | 104 | 138 | 141 | 156 | 159
Corn Density | 0.23919 | g/cm3
|  |  | 3 | 0.06858 | 162.5 | 166 | 200 | 212 | 218 | 221
Flow Rate | 3.24e-05 | m3/min
Corn Bed Depth | 0.02286 | m
Diameter | 0.0254 | m
Area | 0.00050671 | m2
Loading Rate | 0.063942 | m/min
From Bed-Depth Service Time Curves
AZ (adsoprtion zone height) | 0.017 | m
a | 54.68 | h/m
b | -0.98333 | h
v (velocity of AZ) | 0.018288 | m/hr
Cob Utilization | 2.2165 | g/h
Cob Utilization | 53.1965 | g/day
.017 m

## Series Breakthrough Curve
Time (min) | Cout/Cin Column 1 | Cout/Cin Column 2 | Cout/Cin Column 3 | Breakthrough (Cb/Cin) | Exhaustion
0 | 0 | 0 | 0 | 0.060827 | 0.75
3.0864 | 0 | 0 | 0 | 0.060827 | 0.75
6.1728 | 0 | 0 | 0 | 0.060827 | 0.75
9.2593 | 0 | 0 | 0 | 0.060827 | 0.75
12.3457 | 0 | 0 | 0 | 0.060827 | 0.75
15.4321 | 0.10596 | 0 | 0 | 0.060827 | 0.75
18.5185 | 0.12056 | 0 | 0 | 0.060827 | 0.75
21.6049 | 0.1764 | 0 | 0 | 0.060827 | 0.75
24.6914 | 0.20195 | 0 | 0 | 0.060827 | 0.75
27.7778 | 0.21898 | 0 | 0 | 0.060827 | 0.75
30.8642 | 0.24209 | 0 | 0 | 0.060827 | 0.75
33.9506 | 0.27494 | 0 | 0 | 0.060827 | 0.75
37.037 | 0.3163 | 0 | 0 | 0.060827 | 0.75
40.1235 | 0.37713 | 0 | 0 | 0.060827 | 0.75
43.2099 | 0.46959 | 0 | 0 | 0.060827 | 0.75
46.2963 | 0.42214 | 0 | 0 | 0.060827 | 0.75
49.3827 | 0.51095 | 0 | 0 | 0.060827 | 0.75
52.4691 | 0.57786 | 0 | 0 | 0.060827 | 0.75
55.5556 | 0.6326 | 0 | 0 | 0.060827 | 0.75
58.642 | 0.5438 | 0 | 0 | 0.060827 | 0.75
61.7284 | 0.58394 | 0 | 0 | 0.060827 | 0.75
64.8148 | 0.64112 | 0 | 0 | 0.060827 | 0.75
70.9877 | 0.70073 | 0 | 0 | 0.060827 | 0.75
76.3889 | 0.75061 | 0 | 0 | 0.060827 | 0.75
90.7407 |  | 0 | 0 | 0.060827 | 0.75
92.5926 |  | 0 | 0 | 0.060827 | 0.75
94.5988 |  | 0 | 0 | 0.060827 | 0.75
97.6852 |  | 0.061089 | 0 | 0.060827 | 0.75
100.7716 |  | 0.060979 | 0 | 0.060827 | 0.75
103.858 |  | 0.10596 | 0 | 0.060827 | 0.75
106.9444 |  | 0.12056 | 0 | 0.060827 | 0.75
110.0309 |  | 0.1764 | 0 | 0.060827 | 0.75
113.1173 |  | 0.20195 | 0 | 0.060827 | 0.75
116.2037 |  | 0.21898 | 0 | 0.060827 | 0.75
119.2901 |  | 0.24209 | 0 | 0.060827 | 0.75
122.3765 |  | 0.27494 | 0 | 0.060827 | 0.75
125.463 |  | 0.3163 | 0 | 0.060827 | 0.75
128.5494 |  | 0.37713 | 0 | 0.060827 | 0.75
131.6358 |  | 0.46959 | 0 | 0.060827 | 0.75
134.7222 |  | 0.42214 | 0 | 0.060827 | 0.75
137.8086 |  | 0.51095 | 0 | 0.060827 | 0.75
140.8951 |  | 0.57786 | 0 | 0.060827 | 0.75
143.9815 |  | 0.6326 | 0 | 0.060827 | 0.75
147.0679 |  | 0.5438 | 0 | 0.060827 | 0.75
150.1543 |  | 0.58394 | 0 | 0.060827 | 0.75
153.2407 |  | 0.64112 | 0 | 0.060827 | 0.75
156.3272 |  | 0.70073 | 0 | 0.060827 | 0.75
159.4136 |  | 0.75061 | 0 | 0.060827 | 0.75
162.5 |  |  | 0.061089 | 0.060827 | 0.75
165.5864 |  |  | 0.10596 | 0.060827 | 0.75
168.6728 |  |  | 0.12056 | 0.060827 | 0.75
171.7593 |  |  | 0.1764 | 0.060827 | 0.75
174.8457 |  |  | 0.20195 | 0.060827 | 0.75
177.9321 |  |  | 0.21898 | 0.060827 | 0.75
181.0185 |  |  | 0.24209 | 0.060827 | 0.75
184.1049 |  |  | 0.27494 | 0.060827 | 0.75
187.1914 |  |  | 0.3163 | 0.060827 | 0.75
190.2778 |  |  | 0.37713 | 0.060827 | 0.75
193.3642 |  |  | 0.46959 | 0.060827 | 0.75
196.4506 |  |  | 0.42214 | 0.060827 | 0.75
199.537 |  |  | 0.51095 | 0.060827 | 0.75
202.6235 |  |  | 0.57786 | 0.060827 | 0.75
205.7099 |  |  | 0.6326 | 0.060827 | 0.75
208.7963 |  |  | 0.5438 | 0.060827 | 0.75
211.8827 |  |  | 0.58394 | 0.060827 | 0.75
214.9691 |  |  | 0.64112 | 0.060827 | 0.75
218.0556 |  |  | 0.70073 | 0.060827 | 0.75
221.142 |  |  | 0.75061 | 0.060827 | 0.75
|  |  |  | 0.060827 | 0.75

## Pilot Breakthrough Curve
Sample ID | Lab ID | Time (min) | Volume Treated (mL) | Cd Concentration (mg/L) | Cd Concentration (µg/L) | Cout/Cin | Breakthrough (Cb/Cin) | Exhaustion
T0 | 19027-01 |  | N/A- Standard | 0.0822 | 82.2 |  | 0.060827 | 0.75
T1 | 19027-02 | 0 | 0 | ND | 0 | 0 | 0.060827 | 0.75
T3 | 19027-03 | 3.0864 | 100 | ND | 0 | 0 | 0.060827 | 0.75
T5 | 19027-04 | 6.1728 | 200 | ND | 0 | 0 | 0.060827 | 0.75
T7 | 19027-05 | 9.2593 | 300 | ND | 0 | 0 | 0.060827 | 0.75
T9 | 19027-06 | 12.3457 | 400 | ND | 0 | 0 | 0.060827 | 0.75
T11 | 19027-07 | 15.4321 | 500 | 0.00871 | 8.71 | 0.10596 | 0.060827 | 0.75
T13 | 19027-08 | 18.5185 | 600 | 0.00991 | 9.91 | 0.12056 | 0.060827 | 0.75
T15 | 19027-09 | 21.6049 | 700 | 0.0145 | 14.5 | 0.1764 | 0.060827 | 0.75
T17 | 19027-10 | 24.6914 | 800 | 0.0166 | 16.6 | 0.20195 | 0.060827 | 0.75
T19 | 19027-11 | 27.7778 | 900 | 0.018 | 18 | 0.21898 | 0.060827 | 0.75
T21 | 19027-12 | 30.8642 | 1000 | 0.0199 | 19.9 | 0.24209 | 0.060827 | 0.75
T23 | 19027-13 | 33.9506 | 1100 | 0.0226 | 22.6 | 0.27494 | 0.060827 | 0.75
T25 | 19027-14 | 37.037 | 1200 | 0.026 | 26 | 0.3163 | 0.060827 | 0.75
T27 | 19027-15 | 40.1235 | 1300 | 0.031 | 31 | 0.37713 | 0.060827 | 0.75
T29 | 19027-16 | 43.2099 | 1400 | 0.0386 | 38.6 | 0.46959 | 0.060827 | 0.75
T31 | 19027-17 | 46.2963 | 1500 | 0.0347 | 34.7 | 0.42214 | 0.060827 | 0.75
T33 | 19027-18 | 49.3827 | 1600 | 0.042 | 42 | 0.51095 | 0.060827 | 0.75
T35 | 19027-19 | 52.4691 | 1700 | 0.0475 | 47.5 | 0.57786 | 0.060827 | 0.75
T37 | 19027-20 | 55.5556 | 1800 | 0.052 | 52 | 0.6326 | 0.060827 | 0.75
T39 | 19027-21 | 58.642 | 1900 | 0.0447 | 44.7 | 0.5438 | 0.060827 | 0.75
T41 | 19027-22 | 61.7284 | 2000 | 0.048 | 48 | 0.58394 | 0.060827 | 0.75
T43 | 19027-23 | 64.8148 | 2100 | 0.0527 | 52.7 | 0.64112 | 0.060827 | 0.75
T45 | 19027-24 | 70.9877 | 2300 | 0.0576 | 57.6 | 0.70073 | 0.060827 | 0.75
T47 | 19027-25 | 76.3889 | 2475 | 0.0617 | 61.7 | 0.75061 | 0.060827 | 0.75
|  |  | 3000 |  |  |  | 0.060827 | 0.75
Exhaustion: | 75%
Time: | 76.39 | min