## Slide 1: Chiricahua National Monument Septic Design
CENE 486, 5/2/2025
Jeevan Gill, Beizhe Shen, and Nicholas Wakefield
This Photo by Unknown Author is licensed under CC BY-NC-ND

## Slide 2: Project Purpose
Chiricahua NM, 30 miles SE of Wilcox, AZ.
NPS wants to expand volunteer housing
Need new RV pads with delivery & removal hookups.
Expected to be 7 units.
Design a wastewater treatment system
Existing wellhead & treatment building
Client: Sam Bell, NPS Chief of Facilities
TA: Ryan Mahar, CD&E
GI: Dr. Heiderscheidt, NAU
Figure 1. Location Map
Notes: Jeevan

## Slide 3: Project Location and Vicinity Maps
Figure 2. Vicinity Map
Figure 3. Monument Reference Map [4]
Notes: Nick

## Slide 4: Existing Infrastructure
Figure 4. Existing infrastructure
Notes: Nick

## Slide 5: Site Visit and Percolation Testing
Two on-site percolation tests. ​
First test scrapped, second test in best location on site.​
Utilized ASTM D5921​
1 cu. ft. hole.​
Results in table 1.
Percolation test result (Time / inch) | 
Trial number | Time
Trial 1 | 11 minutes 40 seconds
Trial 2 | 12 minutes 38 seconds
Trial 3 | 12 minutes 10 seconds
Table 1 – Percolation Test Results
Rate: 12 minutes, 16 seconds per inch.​
0.081 in/min​
ADEQ R18-9-A310 req. 1-30 mins/inch [1]
Figure 5. Percolation Test Hole
Photo by J. Gill

## Slide 6: Proctor Compaction Testing
Modified Proctor Compaction (ASTM D1557)
Figure 6. Proctor Compaction
Photo by J. Gill
Figure 7. Saturated Sample
Photo by J. Gill
Figure 8. Moisture Content Cans
Photo by J. Gill

## Slide 7: Proctor Compaction Data
Proctor Data |  |  |  |  | 
MODIFIED | 1 (6%) | 2 (9%) | 3 (12%) | 4 (15%) | 5 (18%)
W1 (g) | 4610 |  |  |  | 
D (in) | 4 |  |  |  | 
H (in) | 6.63 |  |  |  | 
W2 (g) | 6571 | 6584 | 6567 | 6497 | 6467
Moisture Content Data |  |  |  |  | 
Can weight (g) | 13.2 | 13.4 | 13.4 | 13.7 | 13.8
Can + wet soil | 50.4 | 48.2 | 47.7 | 58.4 | 64.4
Can + dried soil | 46.9 | 43.4 | 42.6 | 50.6 | 55.2
Where:
W1 = Mold weight + base plate
D = Diameter
H = Height
W2 = Mold + base plate + soil
Figure 9. Proctor Mold
Table 2 – Proctor Test Results
Graph 1 – Moisture Content Graph
Max Dry Density
Optimum Moisture Content

## Slide 8: Potable Design
Figure 10. Septic Wide View

## Slide 9: Potable Design Calculations
Utilized Energy Equation and solved for pressure to determine pressure at various points.
HDPE used system wide, used standard C = 150.
Hazen-Williams equation for determining headloss between points (below).
Table 3 – Pressure at Points
Figure 11. Hazen-Williams Head-loss
Location | End Elevation (ft) | Pressures (psi) | 
 |  | Well @ 40psi | Well @ 60psi
Trailer 1 | 5145.36 | 40.11 | 60.11
Trailer 2 | 5145.92 | 39.79 | 59.79
Trailer 3 | 5144.68 | 39.87 | 59.87
Trailer 4 | 5144.71 | 40.46 | 60.46
Trailer 5 | 5143.20 | 41.05 | 61.05
Trailer 6 | 5141.91 | 41.59 | 61.52
Trailer 7 | 5139.87 | 42.07 | 62.00
Laundry | 5141.49 | 41.37 | 61.37

## Slide 10: On-Site Wastewater Treatment Systems and Scoring
1 - Least Optimum - Installation costs more than $30,000. Spacing requirements do not comply.
2 - Worse – this score's criteria ranges fall between scores one and three.
3 - Neutral - Installation costs fall within the more than $10,000 less than $20,000 range. Spacing requirements require some space.
4 - Better - this score’s criteria ranges fall between the values for scores three and five.
5 - Optimum - Installation costs for a score of five are less than $10,000. Spacing requirements represent not needing space.
Figure 12. Septic and Mound System
Figure 13. RSF System

## Slide 11: Wastewater Treatment System Decision Matrix
Design Decision Matrix |  | Septic System |  | Sand Filter |  | Mound System |  | Biomass Filtration | 
Criteria | Weight | Score | Weighted Score | Score | Weighted Score | Score | Weighted Score | Score | Weighted Score
Maintenance Costs | 2 | 5 | 10 | 3 | 6 | 2 | 4 | 2 | 4
Space Requirements | 3 | 2 | 6 | 5 | 15 | 3 | 9 | 5 | 15
System Longevity | 1 | 4 | 4 | 3 | 3 | 3 | 3 | 2 | 2
Cost of Implementation | 2 | 5 | 10 | 2 | 4 | 4 | 8 | 3 | 6
Total Score |  |  | 30 |  | 28 |  | 24 |  | 27
Table 4 – Decision Matrix

## Slide 12: ADEQ R18-9-A314
Figure 14. Septic System [3]
Table 5 – ADEQ R18-9 Unit Design Flow Table
Wastewater Source | Applicable Unit | Sewage Design Flow per Applicable Unit, (gallons per day)
Airport | Passenger (average daily number) Employee | 4 15
Auto Wash | Facility | Per manufacturer, if consistent with this Chapter
Bar/Lounge | Seat | 30
Barber Shop | Chair | 35
Beauty Parlor | Chair | 100
Bowling Alley (snack bar only) | Lane | 75
Camp Day camp, no cooking facilities Campground, overnight, flush toilets Campground, overnight, flush toilets, and shower Campground, luxury Camp, youth, summer, or seasonal | Camping unit Camping unit Camping unit Person Person | 30 75 150 100-150 50

## Slide 13: Septic System Design
Percolation Test Rate ​ (Minutes per inch) ​ | SAR, Trench, Chamber, and Pit ​ (Gal/day/ft^2) ​
15.0 ​ | 0.50 ​
Design Flow - Units ​ |  |  |  | 
Design Flow Type from A18-9 ​ | Quantity per Unit ​ (GPD) ​ | Unit ​ | Units on Site ​ | Total Consumption (gal./day) ​
Campground, overnight, flush toilets and shower ​ | 150 ​ | Per Site ​ | 7 ​ | 1050 ​
Using R18-9-A310, the SAR (Soil Absorption Ratio) is found below.
Table 6 – SAR Table
Table 7 – Design Flow

## Slide 14: Proposed Infrastructure and On-Site Wastewater Map
Figure 15. Septic System​

## Slide 15: On-Site Wastewater Treatment Map Detail -1
Figure 16. Septic System​ Detail 1

## Slide 16: On-Site Wastewater Treatment Map Detail - 2
Figure 17. Septic System​ Detail 2

## Slide 17: Septic Pipe Hookup
Figure 18. Hookup Detail

## Slide 18: Septic Tank Design – Cross Section
Figure 19. Septic Tank Cross- Section

## Slide 19: Septic Tank Design – Top View
Figure 20. Septic Tank Top View

## Slide 20: Septic Tank Design Data
Internal Design Data | 
Long (ft) | 10
Wide (ft) | 5
Depth (ft) | 6
Volume () | 300
Volume (Gallon) | 2240
External Design Data (Include Internal) | 
Total length (ft) | 11
Total wide (ft) | 6
Total depth (ft) | 8
Volume () | 528
Free Plate | 
Depth (ft) | 1
Internal Design Data | 
Long (ft) | 10
Wide (ft) | 5
Depth (ft) | 6
 | 300
Volume (Gallon) | 2240
External Design Data (Include Internal) | 
Total length (ft) | 11
Total wide (ft) | 6
Total depth (ft) | 8
 | 528
Free Plate | 
Depth (ft) | 1
Table 8 – Septic System Data

## Slide 21: Distribution Box Design
Table 9 – Distribution Box Data
Figure 21. Distribution Box Side View
Figure 22. Distribution Box Top View
Distribution Box | 
Side length (ft) | 2
Outlet number | 6
Inlet number | 1
Outlet spacing(in) | 4

## Slide 22: Leach Field Design
Dimensions are 40 feet by 43 feet.
Perforated HDPE Pipe Throughout
Crushed Stone beneath pipes as filter.
Area above pipe refilled with Earth backfill.
Figure 23. Leach Field Top View
Figure 24. Leach Field Cross-Section

## Slide 23: Leach Field Design Data
Infiltration Trench | 
Long (ft) | 40
Wide (ft) | 3
Depth (ft) | 6
Trench number | 6
Space between trenches (ft) | 5
Leach Field | 
Total length (ft) | 40
Total wide (ft) | 43
Area () | 1720
Infiltration Trench | 
Long (ft) | 40
Wide (ft) | 3
Depth (ft) | 6
Trench number | 6
Space between trenches (ft) | 5
Leach Field | 
Total length (ft) | 40
Total wide (ft) | 43
 | 1720
Table 10 – Leach Field Data

## Slide 24: Cost Estimate - Wastewater
Wastewater Collection System Construction Cost Estimate |  |  |  | 
Component | Unit | Quantity Estimate | Unit Cost ($) | Cost ($)
4'' HDPE Pipe | ft | 870 | 10 | 8,700
4’’ HDPE perforated Pipe | ft | 240 | 10 | 2,400
Septic Tank (2240 gallons) | unit | 1 | 4,500 | 4,500
Distribution Box (2' *2', 7 outlets) | unit | 1 | 200 | 200
Crushed Stone (Leach Field Bedding) | CY | 107 | 65 | 6,955
Earthwork (Excavation) | CY | 161 | 15 | 2,415
Earthwork (Backfill) | CY | 54 | 15 | 810
45-degree bend | unit | 4 | 23 | 92
45-degree wye junction | unit | 7 | 186 | 1,302
45° HDPE Bend (for 90° turn: 2 each) | unit | 14 | 23 | 322
Threaded Cleanout Adapter | unit | 7 | 18 | 126
HDPE Cap | unit | 7 | 7 | 49
Concrete Housekeeping Pad (2'x2') | unit | 7 | 65 | 455
Labor fee |  |  |  | 14,163
 |  |  | Total cost | $42,489
Table 11 – Wastewater cost estimate

## Slide 25: Cost Estimate - Potable
Freshwater Cost Estimate |  |  |  | 
Component | Unit | Quantity Estimate | Unit Cost ($) | Cost ($)
2’’ HDPE pipe | Ft | 363 | 2.2 | 799
1'' HDPE pipe | Ft | 146 | 0.8 | 117
0.75'' HDPE pipe | Ft | 10 | 0.6 | 6
Valve (Brass) | Unit | 8 | 65 | 520
Service Hookups (RV Pads) | Unit | 7 | 150 | 1,050
Earthwork (Excavation) | CY | 4 | 15 | 60
Earthwork (Backfill) | CY | 4 | 15 | 60
1'' 25 Degree Bend | unit | 1 | 6.2 | 7
1'' 45 Degree Bend | unit | 1 | 6.2 | 7
2'' 45 Degree Bend | unit | 4 | 13.2 | 53
2'' 90 Degree Bend | unit | 1 | 7.4 | 8
1'' 90 Degree Bend | unit | 2 | 6.2 | 13
2'' 90 Degree Tee | unit | 6 | 13.2 | 80
2'' to 1'' Fitting | unit | 2 | 9.2 | 19
2'' to 0.75'' Fitting | unit | 5 | 9 | 45
Labor fee |  |  |  | 14,400
 |  |  | Total cost | $17,244
Table 12 – Potable water cost estimate

## Slide 26: Project Impacts
Environmental
Effluent is treated, through septic tank and leach field, removes harmful discharge to the local soil
NPS site, having a smaller site, minimal site disturbance for the local plants or wildlife
Economic
Smaller site area, costs for installing and maintaining this project will be relatively cheap compared to large scale commercial projects
Provides jobs for local workers and park service employees who will live in RV housing
Long-term savings for the NPS, as the low operation and maintenance costs for a septic system
Societal
Public health and local health, as there is no risk of exposure to untreated wastewater or sewage to those living in the area
Seasonal employees positively affected as there is clean and safe water on site, promotes workforce's wellbeing
Volunteers can enjoy the neighboring plants and vegetation being planted on the project site

## Slide 27: Conclusion
Septic system best choice for on-site wastewater treatment.

## Slide 28: References
[1] | ​"Ariz. Admin Code 18-9-A310," [Online]. Available: https://casetext.com/regulation/arizona-administrative-code/title-18-environmental-quality/chapter-9-department-of-environmental-quality-water-pollution-control/article-3-aquifer-protection-permits-general-permits/part-a-general-provisions/section-r18-9-a.
[2] | https://websoilsurvey.nrcs.usda.gov/app/WebSoilSurvey.aspx [Online].
[3] | https://www.cleanearthseptic.com/septic-system-101-how-things-work [Online].
[4] | TITLE 18. ENVIRONMENTAL QUALITY CHAPTER 9. DEPARTMENT OF ENVIRONMENTAL QUALITY WATER POLLUTION CONTROL, [Online]. Available: https://www.maricopa.gov/DocumentCenter/View/7495/Arizona-Administrative-Code-Title-18-Chapter-9-Articles-1-2-3-4-PDF

## Slide 29: Thank you.