## Q (peak hours)
Author - Courtney Hiatt
Description - These calculations are based on the 1997 ASHRAE Fundamentals Handbook used to calculate the cooling load (Qdot) during SRP's peak hours. This is then used to calculate the total energy (Q) used to keep the home cool during that time. This value can then be translated to the mass of material needed to store adequate energy using the formulas for latent and sensible heat.
Formulas 1. Q = U* A*CLTD 2. Qtotal = Qroof + Qwindows + Qwalls
| Initial Data |  |  |  |  | Max Q Values (Btu) |  | Max Q Values (kJ) |  | Max Q Values (kWh) |  |  | Sources
| Latitude | 33.43 |  |  |  | Roof | 62327.1 | Roof | 65755.0905 | Roof | 18.2648 |  | Wall Square Footage: | https://sidingauthority.com/estimation-calculator/
| Longitude | 112.02 | F |  |  | Windows | 9817.5 | Windows | 10357.4625 | Windows | 2.877 |  | Roof Square Footage: | https://bmroofing.com/how-much-does-the-average-roof-replacement-cost/#:~:text=A%20U.S.%20Census%20figure%20notes,is%20approximately%201%2C700%20square%20feet.
| Outdoor Dry Bulb | 110 | F |  |  | Walls | 41214.3 | Walls | 43481.0865 | Walls | 12.0777 |  | Formulas | ASHRAE Fundamentals Handbook
| Outdoor Wet Bulb | 80 | F |  |  | Total | 113358.9 | Total | 119593.6395 | Total | 33.2195
| Daily Range | 23 | F |  |  | Min Q Values (Btu) |  | Min Q Values (kJ) |  | Min Q Values (kWh)
| Area of Wall - North Facing | 395 | ft^2 |  |  | Roof | 42355.5 | Roof | 44685.0525 | Roof | 12.4122
| Area of Wall - South Facing | 395 | ft^2 |  |  | Windows | 9817.5 | Windows | 10357.4625 | Windows | 2.877
| Area of Wall - East Facing | 395 | ft^2 |  |  | Walls | 27593.12 | Walls | 29110.7416 | Walls | 8.0861
| Area of Wall - West Facing | 395 | ft^2 |  |  | Total | 79766.12 | Total | 84153.2566 | Total | 23.3753
| Area of Roof | 1700 | ft^2
| Area of Windows | 100 | ft^2 |  |  | Max Qdot Values (Btu/h) |  | Max Qdot Values (kJ/h) |  | Max Qdot Values (kW)
| U Walls | 0.074 | Btu/h*ft^2*F |  |  | 16194.1286 |  | 17084.8056 |  | 4.7456
| U Roof | 0.066 | Btu/h*ft^2*F |  |  | Min Qdot Values (Btu/h) |  | Min Q Values (kJ/h) |  | Min Qdot Values (kW)
| U Windows | 0.55 | Btu/h*ft^2*F |  |  | 11395.16 |  | 12021.8938 |  | 3.3393
| Min Roof - Assume Roof 14 |  |  |  |  | Min North Wall - Assume Wall 16 |  |  |  | Min East Wall - Assume Wall 16 |  |  |  | Min South Wall - Assume Wall 16 |  |  |  | Min West Wall - Assume Wall 16 |  |  |  | Min Windows (Conduction Load) |  |  |  | Total Min Qdot
| Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) |  | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Q (Btu/hr) | Hour | Q (Btu/hr)
| 14 | 32 | 45.5 | 5105.1 |  | 14 | 9 | 22.5 | 657.675 | 14 | 26 | 39.5 | 1154.585 | 14 | 11 | 24.5 | 716.135 | 14 | 11 | 24.5 | 716.135 | 14 | 13 | 26.5 | 1457.5 | 14 | 9807.13
| 15 | 36 | 49.5 | 5553.9 |  | 15 | 10 | 23.5 | 686.905 | 15 | 28 | 41.5 | 1213.045 | 15 | 14 | 27.5 | 803.825 | 15 | 12 | 25.5 | 745.365 | 15 | 14 | 27.5 | 1512.5 | 15 | 10515.54
| 16 | 39 | 52.5 | 5890.5 |  | 16 | 11 | 24.5 | 716.135 | 16 | 30 | 43.5 | 1271.505 | 16 | 17 | 30.5 | 891.515 | 16 | 14 | 27.5 | 803.825 | 16 | 14 | 27.5 | 1512.5 | 16 | 11085.98
| 17 | 42 | 55.5 | 6227.1 |  | 17 | 13 | 26.5 | 774.595 | 17 | 31 | 44.5 | 1300.735 | 17 | 20 | 33.5 | 979.205 | 17 | 17 | 30.5 | 891.515 | 17 | 13 | 26.5 | 1457.5 | 17 | 11630.65
| 18 | 44 | 57.5 | 6451.5 |  | 18 | 14 | 27.5 | 803.825 | 18 | 31 | 44.5 | 1300.735 | 18 | 23 | 36.5 | 1066.895 | 18 | 20 | 33.5 | 979.205 | 18 | 12 | 25.5 | 1402.5 | 18 | 12004.66
| 19 | 45 | 58.5 | 6563.7 |  | 19 | 16 | 29.5 | 862.285 | 19 | 32 | 45.5 | 1329.965 | 19 | 25 | 38.5 | 1125.355 | 19 | 25 | 38.5 | 1125.355 | 19 | 10 | 23.5 | 1292.5 | 19 | 12299.16
| 20 | 45 | 58.5 | 6563.7 |  | 20 | 17 | 30.5 | 891.515 | 20 | 32 | 45.5 | 1329.965 | 20 | 27 | 40.5 | 1183.815 | 20 | 30 | 43.5 | 1271.505 | 20 | 8 | 21.5 | 1182.5 | 20 | 12423
| Total |  |  | 42355.5 |  | Total |  |  | 5392.935 | Total |  |  | 8900.535 | Total |  |  | 6766.745 | Total |  |  | 6532.905 | Total |  |  | 9817.5 | Average | 11395.16
| Max Roof - Assume Roof 1 |  |  |  |  | Max North Wall - Assume Wall 1 |  |  |  | Max East Wall - Assume Wall 1 |  |  |  | Max South Wall - Assume Wall 1 |  |  |  | Max West Wall - Assume Wall 1 |  |  |  | Max Windows (Conduction Load) |  |  |  | Total Max Qdot
| Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) |  | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Q (Btu/hr) | Hour | Q (Btu/hr)
| 14 | 88 | 101.5 | 11388.3 |  | 14 | 27 | 40.5 | 1183.815 | 14 | 31 | 44.5 | 1300.735 | 14 | 52 | 65.5 | 1914.565 | 14 | 42 | 55.5 | 1622.265 | 14 | 13 | 26.5 | 1457.5 | 14 | 18867.18
| 15 | 88 | 101.5 | 11388.3 |  | 15 | 29 | 42.5 | 1242.275 | 15 | 30 | 43.5 | 1271.505 | 15 | 50 | 63.5 | 1856.105 | 15 | 59 | 72.5 | 2119.175 | 15 | 14 | 27.5 | 1512.5 | 15 | 19389.86
| 16 | 83 | 96.5 | 10827.3 |  | 16 | 29 | 42.5 | 1242.275 | 16 | 30 | 43.5 | 1271.505 | 16 | 44 | 57.5 | 1680.725 | 16 | 73 | 86.5 | 2528.395 | 16 | 14 | 27.5 | 1512.5 | 16 | 19062.7
| 17 | 73 | 86.5 | 9705.3 |  | 17 | 28 | 41.5 | 1213.045 | 17 | 28 | 41.5 | 1213.045 | 17 | 34 | 47.5 | 1388.425 | 17 | 80 | 93.5 | 2733.005 | 17 | 13 | 26.5 | 1457.5 | 17 | 17710.32
| 18 | 60 | 73.5 | 8246.7 |  | 18 | 29 | 42.5 | 1242.275 | 18 | 25 | 38.5 | 1125.355 | 18 | 27 | 40.5 | 1183.815 | 18 | 79 | 92.5 | 2703.775 | 18 | 12 | 25.5 | 1402.5 | 18 | 15904.42
| 19 | 43 | 56.5 | 6339.3 |  | 19 | 27 | 40.5 | 1183.815 | 19 | 20 | 33.5 | 979.205 | 19 | 20 | 33.5 | 979.205 | 19 | 62 | 75.5 | 2206.865 | 19 | 10 | 23.5 | 1292.5 | 19 | 12980.89
| 20 | 26 | 39.5 | 4431.9 |  | 20 | 17 | 30.5 | 891.515 | 20 | 14 | 27.5 | 803.825 | 20 | 14 | 27.5 | 803.825 | 20 | 32 | 45.5 | 1329.965 | 20 | 8 | 21.5 | 1182.5 | 20 | 9443.53
| Total |  |  | 62327.1 |  | Total |  |  | 8199.015 | Total |  |  | 7965.175 | Total |  |  | 9806.665 | Total |  |  | 15243.445 | Total |  |  | 9817.5 | Average | 16194.1286
|  | CLTD values (F) | [7 empty] | CLTD values (F)
| Hour | Roof 14 | Wall 16 North | Wall 16 East | Wall 16 South | Wall 16 West | Windows (Conduction Load) |  | Hour | Roof 1 | Wall 1 North | Wall 1 East | Wall 1 South | Wall 1 West | Windows (Conduction Load)
| 14 | 32 | 9 | 26 | 11 | 11 | 13 |  | 14 | 88 | 27 | 31 | 42 | 11 | 13
| 15 | 36 | 10 | 28 | 14 | 12 | 14 |  | 15 | 88 | 29 | 30 | 59 | 12 | 14
| 16 | 39 | 11 | 30 | 17 | 14 | 14 |  | 16 | 83 | 29 | 30 | 73 | 14 | 14
| 17 | 42 | 13 | 31 | 20 | 17 | 13 |  | 17 | 73 | 28 | 28 | 80 | 17 | 13
| 18 | 44 | 14 | 31 | 23 | 20 | 12 |  | 18 | 60 | 29 | 25 | 79 | 20 | 12
| 19 | 45 | 16 | 32 | 25 | 25 | 10 |  | 19 | 43 | 27 | 20 | 62 | 25 | 10
| 20 | 45 | 17 | 32 | 27 | 30 | 8 |  | 20 | 26 | 17 | 14 | 32 | 30 | 8

## Q (night)
Author - Courtney Hiatt
Description - These calculations are based on the 1997 ASHRAE Fundamentals Handbook used to calculate the cooling load (Qdot) during SRP's peak hours. This is then used to calculate the total energy (Q) used to keep the home cool during that time. This value can then be translated to the mass of material needed to store adequate energy using the formulas for latent and sensible heat.
Formulas 1. Q = U* A*CLTD 2. Qtotal = Qroof + Qwindows + Qwalls
| Initial Data |  |  |  | Min Q Values (Btu) |  | Min Q Values (kJ) |  | Min Q Values (kWh) |  |  | Sources
| Latitude | 33.43 |  |  | Roof | 20476.5 | Roof | 21602.7075 | Roof | 6.0006 |  | Wall Square Footage: | https://sidingauthority.com/estimation-calculator/
| Longitude | 112.02 | F |  | Windows | 8167.5 | Windows | 8616.7125 | Windows | 2.3935 |  | Roof Square Footage: | https://bmroofing.com/how-much-does-the-average-roof-replacement-cost/#:~:text=A%20U.S.%20Census%20figure%20notes,is%20approximately%201%2C700%20square%20feet.
| Outdoor Dry Bulb | 110 | F |  | Walls | 22273.26 | Walls | 23498.2893 | Walls | 6.5271 |  | Formulas | ASHRAE Fundamentals Handbook
| Outdoor Wet Bulb | 80 | F |  | Total | 50917.26 | Total | 53717.7093 | Total | 14.9212
| Daily Range | 23 | F |  | Max Q Values (Btu) |  | Max Q Values (kJ) |  | Max Q Values (kWh)
| Area of Wall - North Facing | 395 | ft^2 |  | Roof | 59297.7 | Roof | 62559.0735 | Roof | 17.377
| Area of Wall - South Facing | 395 | ft^2 |  | Windows | 8167.5 | Windows | 8616.7125 | Windows | 2.3935
| Area of Wall - East Facing | 395 | ft^2 |  | Walls | 47995.66 | Walls | 50635.4213 | Walls | 14.065
| Area of Wall - West Facing | 395 | ft^2 |  | Total | 115460.86 | Total | 121811.2073 | Total | 33.8355
| Area of Roof | 1700 | ft^2
| Area of Windows | 100 | ft^2 |  | Min Qdot Values (Btu/h) |  | Min Qdot Values (kJ/h) |  | Min Qdot Values (kW)
| U Walls | 0.074 | Btu/h*ft^2*F |  | 4628.8418 |  | 4883.4281 |  | 1.3565
| U Roof | 0.066 | Btu/h*ft^2*F |  | Max Qdot Values (Btu/h) |  | Max Q Values (kJ/h) |  | Max Qdot Values (kW)
| U Windows | 0.55 | Btu/h*ft^2*F |  | 10496.4418 |  | 11073.7461 |  | 3.076
| Max Roof - Assume Roof 14 |  |  |  | Max North Wall - Assume Wall 16 |  |  |  | Max East Wall - Assume Wall 16 |  |  |  | Max South Wall - Assume Wall 16 |  |  |  | Max West Wall - Assume Wall 16 |  |  |  | Max Windows (Conduction Load) |  |  |  | Total Qdot
| Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Q (Btu/hr) | Hour | Q (Btu/hr)
| 20 | 45 | 58.5 | 6563.7 | 20 | 17 | 30.5 | 891.515 | 20 | 32 | 45.5 | 1329.965 | 20 | 27 | 40.5 | 1183.815 | 20 | 30 | 43.5 | 1271.505 | 20 |  | 13.5 | 742.5 | 20 | 11983
| 21 | 44 | 57.5 | 6451.5 | 21 | 18 | 31.5 | 920.745 | 21 | 31 | 44.5 | 1300.735 | 21 | 27 | 40.5 | 1183.815 | 21 | 34 | 47.5 | 1388.425 | 21 |  | 13.5 | 742.5 | 21 | 11987.72
| 22 | 42 | 55.5 | 6227.1 | 22 | 19 | 32.5 | 949.975 | 22 | 30 | 43.5 | 1271.505 | 22 | 27 | 40.5 | 1183.815 | 22 | 37 | 50.5 | 1476.115 | 22 |  | 13.5 | 742.5 | 22 | 11851.01
| 23 | 40 | 53.5 | 6002.7 | 23 | 19 | 32.5 | 949.975 | 23 | 29 | 42.5 | 1242.275 | 23 | 27 | 40.5 | 1183.815 | 23 | 38 | 51.5 | 1505.345 | 23 |  | 13.5 | 742.5 | 23 | 11626.61
| 24 | 37 | 50.5 | 5666.1 | 24 | 19 | 32.5 | 949.975 | 24 | 27 | 40.5 | 1183.815 | 24 | 25 | 38.5 | 1125.355 | 24 | 37 | 50.5 | 1476.115 | 24 |  | 13.5 | 742.5 | 24 | 11143.86
| 1 | 35 | 48.5 | 5441.7 | 1 | 18 | 31.5 | 920.745 | 1 | 25 | 38.5 | 1125.355 | 1 | 24 | 37.5 | 1096.125 | 1 | 36 | 49.5 | 1446.885 | 1 |  | 13.5 | 742.5 | 1 | 10773.31
| 2 | 32 | 45.5 | 5105.1 | 2 | 17 | 30.5 | 891.515 | 2 | 23 | 36.5 | 1066.895 | 2 | 22 | 35.5 | 1037.665 | 2 | 33 | 46.5 | 1359.195 | 2 |  | 13.5 | 742.5 | 2 | 10202.87
| 3 | 30 | 43.5 | 4880.7 | 3 | 16 | 29.5 | 862.285 | 3 | 21 | 34.5 | 1008.435 | 3 | 20 | 33.5 | 979.205 | 3 | 31 | 44.5 | 1300.735 | 3 |  | 13.5 | 742.5 | 3 | 9773.86
| 4 | 27 | 40.5 | 4544.1 | 4 | 14 | 27.5 | 803.825 | 4 | 19 | 32.5 | 949.975 | 4 | 18 | 31.5 | 920.745 | 4 | 28 | 41.5 | 1213.045 | 4 |  | 13.5 | 742.5 | 4 | 9174.19
| 5 | 25 | 38.5 | 4319.7 | 5 | 13 | 26.5 | 774.595 | 5 | 17 | 30.5 | 891.515 | 5 | 16 | 29.5 | 862.285 | 5 | 25 | 38.5 | 1125.355 | 5 |  | 13.5 | 742.5 | 5 | 8715.95
| 6 | 23 | 36.5 | 4095.3 | 6 | 11 | 24.5 | 716.135 | 6 | 15 | 28.5 | 833.055 | 6 | 14 | 27.5 | 803.825 | 6 | 22 | 35.5 | 1037.665 | 6 |  | 13.5 | 742.5 | 6 | 8228.48
| Total |  |  | 59297.7 | Total |  |  | 9631.285 | Total |  |  | 12203.525 | Total |  |  | 11560.465 | Total |  |  | 14600.385 | Total |  |  | 8167.5 | Average | 10496.4418
| Min Roof - Assume Roof 1 |  |  |  | Min North Wall - Assume Wall 1 |  |  |  | Min East Wall - Assume Wall 1 |  |  |  | Min South Wall - Assume Wall 1 |  |  |  | Min West Wall - Assume Wall 1 |  |  |  | Min Windows (Conduction Load) |  |  |  | Total Qdot
| Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Qdot (Btu/hr) | Hour | CLTD (F) | CLTD corrected (F) | Q (Btu/hr) | Hour | Q (Btu/hr)
| 20 | 26 | 39.5 | 4431.9 | 20 | 17 | 30.5 | 891.515 | 20 | 14 | 27.5 | 803.825 | 20 | 14 | 27.5 | 803.825 | 20 | 32 | 45.5 | 1329.965 | 20 |  | 13.5 | 742.5 | 20 | 9003.53
| 21 | 15 | 28.5 | 3197.7 | 21 | 11 | 24.5 | 716.135 | 21 | 10 | 23.5 | 686.905 | 21 | 10 | 23.5 | 686.905 | 21 | 16 | 29.5 | 862.285 | 21 |  | 13.5 | 742.5 | 21 | 6892.43
| 22 | 9 | 22.5 | 2524.5 | 22 | 7 | 20.5 | 599.215 | 22 | 7 | 20.5 | 599.215 | 22 | 7 | 20.5 | 599.215 | 22 | 9 | 22.5 | 657.675 | 22 |  | 13.5 | 742.5 | 22 | 5722.32
| 23 | 5 | 18.5 | 2075.7 | 23 | 5 | 18.5 | 540.755 | 23 | 5 | 18.5 | 540.755 | 23 | 5 | 18.5 | 540.755 | 23 | 6 | 19.5 | 569.985 | 23 |  | 13.5 | 742.5 | 23 | 5010.45
| 24 | 2 | 15.5 | 1739.1 | 24 | 3 | 16.5 | 482.295 | 24 | 3 | 16.5 | 482.295 | 24 | 3 | 16.5 | 482.295 | 24 | 3 | 16.5 | 482.295 | 24 |  | 13.5 | 742.5 | 24 | 4410.78
| 1 | 0 | 13.5 | 1514.7 | 1 | 1 | 14.5 | 423.835 | 1 | 1 | 14.5 | 423.835 | 1 | 1 | 14.5 | 423.835 | 1 | 2 | 15.5 | 453.065 | 1 |  | 13.5 | 742.5 | 1 | 3981.77
| 2 | -2 | 11.5 | 1290.3 | 2 | 0 | 13.5 | 394.605 | 2 | 0 | 13.5 | 394.605 | 2 | 0 | 13.5 | 394.605 | 2 | 1 | 14.5 | 423.835 | 2 |  | 13.5 | 742.5 | 2 | 3640.45
| 3 | -4 | 9.5 | 1065.9 | 3 | -1 | 12.5 | 365.375 | 3 | -1 | 12.5 | 365.375 | 3 | -1 | 12.5 | 365.375 | 3 | -1 | 12.5 | 365.375 | 3 |  | 13.5 | 742.5 | 3 | 3269.9
| 4 | -5 | 8.5 | 953.7 | 4 | -2 | 11.5 | 336.145 | 4 | -2 | 11.5 | 336.145 | 4 | -2 | 11.5 | 336.145 | 4 | -2 | 11.5 | 336.145 | 4 |  | 13.5 | 742.5 | 4 | 3040.78
| 5 | -6 | 7.5 | 841.5 | 5 | -3 | 10.5 | 306.915 | 5 | -2 | 11.5 | 336.145 | 5 | -3 | 10.5 | 306.915 | 5 | -2 | 11.5 | 336.145 | 5 |  | 13.5 | 742.5 | 5 | 2870.12
| 6 | -6 | 7.5 | 841.5 | 6 | -1 | 12.5 | 365.375 | 6 | 2 | 15.5 | 453.065 | 6 | -2 | 11.5 | 336.145 | 6 | -2 | 11.5 | 336.145 | 6 |  | 13.5 | 742.5 | 6 | 3074.73
| Total |  |  | 20476.5 | Total |  |  | 5422.165 | Total |  |  | 5422.165 | Total |  |  | 5276.015 | Total |  |  | 6152.915 | Total |  |  | 8167.5 | Average | 4628.8418